{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["废水"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"废水","index":0,"n_rows":17,"n_cols":18,"rows_kept":17,"merged":[[0,0,0,18],[1,7,1,18],[2,3,2,4],[2,5,2,6],[2,7,2,8],[2,9,2,10],[2,11,2,12],[2,13,2,14],[2,15,2,16],[2,17,2,18],[3,3,3,4],[3,5,3,6],[3,7,3,8],[3,9,3,10],[3,11,3,12],[3,13,3,14],[3,15,3,16],[3,17,3,18],[4,0,4,2],[4,3,4,4],[4,5,4,6],[4,7,4,8],[4,9,4,10],[4,11,4,12],[4,13,4,14],[4,15,4,16],[4,17,4,18],[5,0,5,2],[5,3,5,4],[5,5,5,6],[5,7,5,8],[5,9,5,10],[5,11,5,12],[5,13,5,14],[5,15,5,16],[5,17,5,18],[6,3,6,4],[6,5,6,6],[6,7,6,8],[6,9,6,10],[6,11,6,12],[6,13,6,14],[6,15,6,16],[6,17,6,18],[7,0,7,2],[7,3,7,4],[7,5,7,6],[7,7,7,8],[7,9,7,10],[7,11,7,12],[7,13,7,14],[7,15,7,16],[7,17,7,18],[8,0,8,2],[8,3,8,4],[8,5,8,6],[8,7,8,8],[8,9,8,10],[8,11,8,12],[8,13,8,14],[8,15,8,16],[8,17,8,18],[9,3,9,4],[9,5,9,6],[9,7,9,8],[9,9,9,10],[9,11,9,12],[9,13,9,14],[9,15,9,16],[9,17,9,18],[10,3,10,4],[10,5,10,6],[10,7,10,8],[10,9,10,10],[10,11,10,12],[10,13,10,14],[10,15,10,16],[10,17,10,18],[11,0,11,2],[11,3,11,4],[11,5,11,6],[11,7,11,8],[11,9,11,10],[11,11,11,12],[11,13,11,14],[11,15,11,16],[11,17,11,18],[12,0,12,2],[12,3,12,4],[12,5,12,6],[12,7,12,8],[12,9,12,10],[12,11,12,12],[12,13,12,14],[12,15,12,16],[12,17,12,18],[13,3,13,4],[13,5,13,6],[13,7,13,8],[13,9,13,10],[13,11,13,12],[13,13,13,14],[13,15,13,16],[13,17,13,18],[14,0,14,2],[14,3,14,4],[14,5,14,6],[14,7,14,8],[14,9,14,10],[14,11,14,12],[14,13,14,14],[14,15,14,16],[14,17,14,18],[15,0,15,2],[15,3,15,4],[15,5,15,6],[15,7,15,8],[15,9,15,10],[15,11,15,12],[15,13,15,14],[15,15,15,16],[15,17,15,18],[16,0,16,18]],"flags":["formulas_cached_only"]}
["附表1：               惠州市2014年第3季度生活垃圾处理企业废水监督性监测结果"]
[{"$nulls":7},"单位:毫克/升（PH值：无量纲、粪大肠菌群：个/升除外）"]
["企业名称","监测日期","监测点位","pH值",null,"悬浮物",null,"化学需氧量",null,"氨氮",null,"总氮",null,"总磷",null,"总铬",null,"六价铬"]
["惠州市垃圾填埋场\n（惠城区填埋场）","2014-09-01","渗滤液处理后排口",6.15,null,8,null,16,null,11.1,null,32.4,null,0.06,null,"0.004L",null,"0.004L"]
["《生活垃圾填埋场垃圾控制标准》GB16889-2008、广东省地方标准《水污染物排放限值》(DB44/26-2001)第二时段一级标准",null,null,"6—9",null,30,null,100,null,25,null,40,null,3,null,0.1,null,0.05]
["评价",null,null,"达标",null,"达标",null,"达标",null,"达标",null,"达标",null,"达标",null,"达标",null,"达标"]
["惠阳区山子顶填埋场","2014-09-01","渗滤液处理后排口",7.04,null,9,null,214,null,39.8,null,120,null,0.13,null,"0.004L",null,"0.004L"]
["《生活垃圾填埋场垃圾控制标准》GB16889-2008、广东省地方标准《水污染物排放限值》(DB44/26-2001)第二时段一级标准",null,null,"6—9",null,30,null,100,null,25,null,40,null,3,null,0.1,null,0.05]
["评价",null,null,"达标",null,"达标",null,"超标1.1倍",null,"超标0.6倍",null,"超标2.0倍",null,"达标",null,"达标",null,"达标"]
["企业名称","监测日期","监测点位","砷",null,"镉",null,"铅",null,"汞",null,"粪大肠菌群",null,"五日生化需氧量",null,"色度"]
["惠州市垃圾填埋场\n（惠城区填埋场）","2014-09-01","渗滤液处理后排口","0.0004L",null,"0.00006L",null,"0.00007L",null,"0.00004L",null,"<20",null,4,null,8]
["《生活垃圾填埋场垃圾控制标准》GB16889-2008",null,null,0.1,null,0.01,null,0.1,null,0.001,null,10000,null,30,null,40]
["评价",null,null,"达标",null,"达标",null,"达标",null,"达标",null,"达标",null,"达标",null,"达标"]
["惠阳区山子顶填埋场","2014-09-01","渗滤液处理后排口","0.0004L",null,"0.00006L",null,"0.00007L",null,"0.00004L",null,"<20",null,60,null,2]
["《生活垃圾填埋场垃圾控制标准》GB16889-2008",null,null,0.1,null,0.01,null,0.1,null,0.001,null,10000,null,30,null,40]
["评价",null,null,"达标",null,"达标",null,"达标",null,"达标",null,"达标",null,"超标1.0倍",null,"达标"]
["备注:1.惠州市垃圾填埋场（惠城区填埋场）和惠阳区山子顶填埋场的地下水和废气均未通过验收；\n     2.惠城区焚烧发电厂、博罗县垃圾填埋场、龙门县垃圾填埋场和惠东县垃圾填埋场均未通过验收。"]